## Calculations
PRESSURE MANIFOLD CALCULATION TOOL
Missouri Department of Health and Senior Services, Onsite Wastewater Treatment Program
| ABSORPTION SYSTEM CALCULATIONS | Manual Calculation Formula | Calculated Output | Input | Units
Residential
1 | Number of units (bedrooms, seats, etc.) | Design input |  |  | Bedrooms
2 | Flow per unit (Table 2A, Onsite Minimum Standards) | Design input |  | 120 | gpd
3 | Design daily wastewater flow | Line1 x Line2 |  |  | gpd
4 | Trench depth | Design input |  | 18 | inches
5 | Soil loading rate from soil report | Design input |  |  | gpd/sq.ft.
6 | Trench bottom area (minimum) | Line3 / Line5 |  |  | sq.ft. |  |  | Select
7 | Effective trench width, based on type of trench material | Design input |  | Select | feet |  | 1.5 | 18" gravel
8 | Total trench length (minimum) | Line6 / Line7 |  |  | feet | 6 | 2 | 24" gravel
9 | Number of zones | Line7 / 1000 (Round up) |  |  |  | 6 | 2 | 15" chamber
10 | Design daily wastewater flow per zone | Line3 / Line9 |  |  | gpd |  | 2 | 12" EPS bundle
11 | Length of trench per zone (minimum) | Line7 / Line9 |  |  | feet |  | 2.083 | 10" gravelless
12 | Number of trenches per zone | Line11 / 100 (Round up) |  |  |  |  | 2.333 | 22" chamber
13 | Trench length, average | Line11 / Line12 |  |  | feet |  | 3 | 36" gravel
14 | Zone dose volume | 0.5 x Line11 |  |  | gallons |  | 3.5 | 34" chamber
| FLOW CALCULATIONS | [5 empty] | #N/A
15 | Operating head | Design input |  | 4 | feet
16 | Orifice (hole) diameter | Design input |  | 0.25 | inches | 0.15625
17 | Flow rate per orifice (see Table 2) | 11.79 x (Line16)2 x √Line15 |  |  | gpm | 0.1875
18 | Flow rate per zone (target) | Design input |  | 25 | gpm | 0.25
19 | Number of orifices per zone (approx.) | Line18 / Line17(Round) |  |  |  | 0.3125
20 | Number of orifices per lateral (equal length) | Line19 / Line12(Round) |  |  |  | 0.375
21 | Flow rate per lateral (equal length) | Line17 x Line20 |  |  | gpm | 0.4375
22 | Number of orifices per zone (equal length laterals) | Line20 x Line12 |  |  |  | 0.5
23 | Flow rate per zone (equal length laterals) | Line17 x Line22 |  |  | gpm | 0.5625
24 | Diameter of supply line | From Table 4 |  |  | inches | 0.625
25 | Type of PVC pipe | Design input |  | 40 |  | 0.6875
26 | Velocity in supply/manifold pipe | Check Tables 1, 4 |  |  | feet/sec | 0.75
27 | Feet of lateral per orifice | Line13 / Line20 |  |  | feet
28 | Trench length tolerance (plus or minus, max) | 0.05 x Line24 |  |  | (±) feet
TIMER CONTROL CALCULATIONS
29 | Dose cycles per day (zone) | Line10 / Line14
30 | Dose cycles per day (total) | Line3 / Line14
31 | Dose time ON each cycle | Line14 / Line23 |  |  | minutes
32 | Time OFF between doses | 1440 / Line30 - Line31 |  |  | minutes
33 | Pump run time per day (approx.) | Line30 x Line31 |  |  | minutes
TOTAL DYNAMIC HEAD CALCULATIONS
34 | ELEVATION HEAD | Determine at site |  |  | feet
35 | Length of supply line | From site layout |  |  | feet length
36 | Equivalent length of fittings, total | From mfg. or SSMPA tables |  |  | feet length
37 | Total equivalent length of supply line | Line35 + Line36 (round up) |  |  | feet length
38 | Supply line friction head / 100 feet | From Table 1a or 1b |  |  | feet
39 | Supply line friction head | Line38 x Line37 /100 |  |  | feet
40 | Add on friction (if any) | From component supplier(s) |  |  | feet
41 | FRICTION HEAD | Line39 + Line40 |  |  | feet
42 | OPERATING HEAD | Line15 |  |  | feet
43 | TDH | Line34 + Line41 + Line42 |  |  | feet
MINIMUM PUMP CAPACITY REQUIRED
44 | Flow capacity | Line23 + 2 |  |  | gpm
45 | Head capacity | Line43 |  |  | feet
Note on C7: Check minimum standards Table 2A
Note on C8: Calculate flows from multiple sources separately and enter total in input column
Note on C9: 18" recommended (18" - 30" allowed); check with local authority about shallow placement modifications
Note on C10: Generally, don't exceed lowest reported rate between the ground surface and 12 inches below the trench (Line2 +12")
Note on C11: Trench bottom area can exceed calculated minimum for a more conservative design
Note on C12: Narrow trenches are recommended to better use the available soil absorption area
Note on C13: Trench length can exceed calculated minimum for a more conservative design
Note on C14: Should limit to less than 1,000 feet of trench per zone. However, more than 6 zones would require a distribution method other than an alternating valve, such as solenoid valves or duplex pumps.
Note on C15: If demand dosing is used, zones will receive equal dose volumes and should be equal in size
Note on C16: Use separate sheets for multiple zones with different trench lengths
Note on C18: Generally, round up to use full length of trench product
Note on C17: Use equal trench lengths if possible, and longest trenches, up to 100 feet, that will fit the site. Minimum of two required
Note on C19: 1/2 gallon per foot of trench, recommended; add volume needed to fill supply line if it drains back to pump tank
Note on C21: Set operating pressure with a valve on each lateral line. Use between 2 feet and 8 feet. (default is 4 feet)
Note on C22: Use to optimize pump flow capacity (default is 1/4-inch)
Note on C23: Read from Table or calculate
Note on C24: Initial value used to help optimize pump capacity and cycle time. Compare pump manufacturer's cycle time recommendations with Line31. Confirm actual flow capacity (Line44) with pump performance curve.
Note on C25: Initial value used to select actual number of orifices per lateral
Note on C26: Use reason when selecting a different number of orifices, as it will affect required pump capacity
Note on C29: Actual flow. 10 to 40 gpm is typical. Confirm sufficient pump capacity (line44 and 45) using pump performance curve.
Note on C33: Only used to proportion distribution in unequal length trenches in a zone
Note on C34: For unequal length trenches, length per orifice should not vary by more than 5%
Note on C42: Difference in elevation (vertical distance) from low water level in pump tank to high point in pressure system
Note on C36: Typically 2 or less doses per day and should not exceed 4 doses
Note on C38: Add time needed to fill supply line if it drains back to pump tank. In the field, you can start with a drained system and time how long it takes to start to discharge at farthest lateral.
Note on C37: Total doses for all zones
Note on C40: Total pump run time not including time needed to fill supply line
Note on C45: Round up to nearest 10 feet
Note on C48: Pressure losses in filters, alternating valves, etc. (if in psi, multiply by 2.31 to obtain feet of head)
Note on C53: Zone flow rate plus allowance of 2 gpm for flow through 5/32" siphon break or weep hole
Note on C6: Check minimum standards Table 2A
Note on C30: Select pipe size for which flow rate (Line23) results in between 2 and 5 feet per second (fps)
Note on C43: Length of supply/manifold pipe from pump to the last lateral line
Note on C44: Recommend using tables, such as from pipe manufacturer or SSPMA. If tables are used, carry manual calculations through line 43. (Calculator estimates equivalent length at 20% of straight length of supply/manifold pipe; be sure to include other losses on Line40.)
Note on C54: When flow and head capacity are plotted on a pump's performance curve, that point must fall below the curve
Note on C47: Calculated value assumes equivalent length of fittings = 20% of the length of the supply pipe. Use with caution and be sure to include any additional friction in Line40
Note on C31: Schedule 40 for example

## Notes, Instructions
PRESSURE MANIFOLD CALCULATION SHEET INSTRUCTIONS
This calculator is a tool and not intended to substitute for sound design judgement. It is not the only method for
designing pressure manifold systems. Site factors may dictate different trench lengths or other modifications.
Comply with all state and local standards and permit requirements.
See manifold schematic diagrams below.
MANUAL CALCULATIONS:
A | Calculate using line# formulas and tables. Double check manual calculations.
B | Defaults are provided below as a starting point. Adjust default numbers to optimize pump requirements or to use a prefered pump.
ELECTRONIC CALCULATIONS:
A | Click on Calculations Sheet tab. For new calculations, you can click the reset button to start with the default numbers.
B | Enter data in the ORANGE cells. (Use 'Enter' or the down arrow key to move to next cell. Use "Backspace" to clear a cell)
C | Defaults are provided as a starting point. Adjust default numbers to optimize pump requirements or to work with a prefered pump.
D | Enter data in the yellow cells (optional), to adjust for site conditions or to make the design more conservative. For example, to use
shorter trenches, increase total length, or round up trench lengths. Entries less than the minimum calculated values are not allowed.
E | Use of the timer control calculations is optional, but recommended.
F | As an alternative to completing the TDH calculations, pump suppliers can assist if you provide the site elevations and supply line length.
G | Use buttons at top of calculation sheet to print worksheets.
| ABSORPTION SYSTEM CALCULATIONS | Notes/Recommendations
1 | Number of units | Check Minimum Construction Standards Table 2A in the Onsite Sewage Rule
2 | Flow per unit | Check Minimum Construction Standards Table 2A in the Onsite Sewage Rule
3 | Design daily wastewater flow | Calculate flows from multiple sources separately and enter total in input column
4 | Trench depth | 18" recommended (18" - 30" allowed); check with local authority about shallow placement modifications
5 | Soil loading rate from soil report | Generally, don't exceed lowest reported rate between the ground surface and 12 inches below the trench (Line4 +12")
6 | Trench bottom area (minimum) | Trench bottom area can exceed calculated minimum for a more conservative design
7 | Effective trench width | Narrow trenches are recommended to better use the available soil absorption area
8 | Total trench length (minimum) | Trench length can exceed calculated minimum for a more conservative design
9 | Number of zones | Should limit to 1,000 feet of trench per zone. However, more than 6 zones would require a dist. method other than an alternating valve, such as solenoid valvess or duplex pumps.
10 | Design daily wastewater flow per zone | If demand dosing is used, zones will receive equal dose volumes and should be equal in size
11 | Length of trench per zone | Use separate sheets for multiple zones with different trench lengths
12 | Number of trenches per zone | Use equal trench lengths if possible, and longest trenches, up to 100 feet, that will fit the site. A minimum of two trenches is required
13 | Trench length, average (minimum) | Generally, round up to use full length of trench product
14 | Zone dose volume | 1/2 gallon per foot of trench, recommended; add volume needed to fill supply line if it drains back to pump tank
FLOW CALCULATIONS
15 | Operating head | Set operating pressure with a valve on each lateral line. Use between 2 feet and 8 feet. (Default is 4 feet)
16 | Orifice (hole) diameter | Use to optimize pump flow capacity (Default is 1/4-inch)
17 | Flow rate per orifice (see Table 2) | Read from Table 2 or calculate using the formula provided
18 | Flow rate per zone (target) | Initial value used to help optimize pump capacity and cycle time. Compare pump manufacturer's cycle time recommendations with Line31. Confirm actual flow capacity (Line44) with pump performance curve. (Default is 25 gpm)
19 | Number of orifices per zone (approx.) | Initial value used to select actual number of orifices per lateral
20 | Number of orifices per lateral (equal length) | Use caution in selecting a different number of orfices, as it will affect required pump capacity
21 | Flow rate per lateral (equal length)
22 | Number of orifices per zone
23 | Flow rate per zone | Actual flow. 10 to 40 gpm is typical. Confirm sufficient pump capacity (line44 and 45) using pump performance curve.
24 | Diameter of supply line | Select pipe size for which flow rate (Line23) results in between 2 and 5 feet/second (fps)
25 | Type of PVC pipe | Schedule 40 for example
26 | Velocity in supply/manifold pipe | If velocity < 2 fps, smaller pipe is recommended; if > 5 fps, larger pipe is recommended
27 | Feet of lateral per orifice | Only used to proportion distribution in unequal length trenches in a zone (see next note)
28 | Trench length tolerance (plus or minus, max) | For unequal length trenches, the length per orifice should not vary by more than 5%
| TIMER CONTROL CALCULATIONS | Recommended as an alternative to demand dosing
29 | Dose cycles per day (zone) | Typically less than 2 doses and should not exceed 4 doses
30 | Dose cycles per day (total) | Total doses for all zones
31 | Dose time ON each cycle | Add time needed to fill supply line if it drains back to pump tank. In the field, you can start with a drained system and time how long it takes to start to discharge at farthest lateral.
32 | Time OFF between doses
33 | Pump run time per day (approx.) | Total pump run time not including time needed to fill supply line
TOTAL DYNAMIC HEAD CALCULATIONS
34 | Elevation head | Difference in elevation (vertical distance) from low water level in pump tank to high point in pressure system
35 | Length of supply line | Length of supply/manifold pipe from pump to the last lateral line
36 | Equivalent length of fittings, total | Recommend using tables, such as from pipe manufacturer or SSPMA. If tables are used, carry manual calculations through line 45. (Calculator estimates equivalent length at 20% of straight length of supply/manifold pipe; be sure to include other losses on Line40.)
37 | Total equivalent length of supply line | Round up to nearest 10 feet
38 | Supply line friction head / 100 feet
39 | Supply line friction head
40 | Add on friction (if any) | Pressure losses in filters, alternating valves, etc. (if in psi, multiply by 2.31 to obtain feet)
41 | Friction head | Use equivalent length of fittings can be more accurate. Compare with calculated value.
42 | Operating head
43 | TDH | If friction is calculated manually using equivalent lengths of fittings, enter TDH on line 45
MINIMUM PUMP CAPACITY REQUIRED
44 | Flow capacity | Zone flow rate plus allowance for flow through 5/32" siphon break or weep hole
45 | Head capacity | When flow and head capacity are plotted on a pump's performance curve, that point must fall below the curve
INSTALLATION
•1 Manifold line with tee at each lateral
•2 Valve used to adjust pressure at each lateral
•3 Tee with threaded adapter to attach standpipe or a cap with a hole
•4 Yard box for access
•5 Dam to prevent effluent from draining into manifold trench
•6 Capped pipe with drilled holes
•7 Any accepted conventional gravity trench material or product
Install system with a standpipe, or a cap with a hole drilled in it, at #3. Use valve,
#2, to adjust equal head or squirt height in each lateral. Install solid caps at #3.
The manifold and supply pipes should drain completely, either back to the
pump tank or to the trenches
1
2
3
4
5
6
7
Photo example of short pipe with 4 orifices to insert into a gravity lateral trench system
Schematic showing components of manifold and short pipe into a gravity lateral trench
Diagram of manifold system with 3 conventional gravity trenches

## Tables
P V C PIPE TABLES
Table 1a:
Pressure Loss per 100-feet of Schedule 40 PVC and Velocity
as a function of flow rate and nominal pipe diameter in inches
|  | 0.5 |  |  | 0.75 |  |  | 1 |  |  | 1.25 |  |  | 1.5
Flow |  | Pressure Drop |  | Velocity | Pressure Drop |  | Velocity | Pressure Drop |  | Velocity | Pressure Drop |  | Velocity | Pressure Drop |  | Velocity
gph | gpm | feet | psi | fps | feet | psi | fps | feet | psi | fps | feet | psi | fps | feet | psi | fps
60 | 1 | 0.98407 | 0.426 | 1.0559 | 0.25009 | 0.10826 | 0.60166 | 0.077158 | 0.033402 | 0.37124
120 | 2 | 3.5525 | 1.55 | 2.1118 | 0.90283 | 0.39084 | 1.2033 | 0.27854 | 0.12058 | 0.74248 | 0.073238 | 0.031705 | 0.42902
180 | 3 | 7.5276 | 3.27 | 3.1677 | 1.9131 | 0.82816 | 1.805 | 0.59022 | 0.2555 | 1.1137 | 0.15519 | 0.067181 | 0.64353 | 0.073242 | 0.031706 | 0.4728
240 | 4 | 12.8245 | 5.57 | 4.2236 | 3.2592 | 1.4109 | 2.4067 | 1.0055 | 0.4353 | 1.485 | 0.26439 | 0.11445 | 0.85804 | 0.12478 | 0.054017 | 0.6304
300 | 5 | 19.3874 | 8.42 | 5.2796 | 4.9271 | 2.1329 | 3.0083 | 1.5201 | 0.65806 | 1.8562 | 0.39969 | 0.17303 | 1.0726 | 0.18864 | 0.08166 | 0.788
360 | 6 | 27.1746 | 11.81 | 6.3355 | 6.9061 | 2.9897 | 3.61 | 2.1307 | 0.92237 | 2.2274 | 0.56023 | 0.24252 | 1.2871 | 0.2644 | 0.11446 | 0.9456
480 | 8 | 46.2966 | 20.1 | 8.4473 | 11.7658 | 5.0934 | 4.8133 | 3.63 | 1.5714 | 2.9699 | 0.95445 | 0.41318 | 1.7161 | 0.45046 | 0.195 | 1.2608
600 | 10 |  |  |  | 17.7868 | 7.6999 | 6.0166 | 5.4876 | 2.3756 | 3.7124 | 1.4429 | 0.62462 | 2.1451 | 0.68097 | 0.29479 | 1.576
900 | 15 |  |  |  | 37.6894 | 16.3158 | 9.0249 | 11.6279 | 5.0337 | 5.5686 | 3.0574 | 1.3235 | 3.2177 | 1.443 | 0.62465 | 2.364
1200 | 20 | [6 empty] | 19.8102 | 8.5759 | 7.4248 | 5.2088 | 2.2549 | 4.2902 | 2.4583 | 1.0642 | 3.152
1500 | 25 | [6 empty] | 29.9479 | 12.9645 | 9.281 | 7.8743 | 3.4088 | 5.3628 | 3.7163 | 1.6088 | 3.94
1800 | 30 | [9 empty] | 11.0372 | 4.778 | 6.4353 | 5.2091 | 2.255 | 4.728
2100 | 35 | [9 empty] | 14.6839 | 6.3567 | 7.5079 | 6.9302 | 3.0001 | 5.516
2400 | 40 | [9 empty] | 18.8037 | 8.1401 | 8.5804 | 8.8745 | 3.8418 | 6.304
2700 | 45 | [9 empty] | 23.3872 | 10.1243 | 9.653 | 11.0377 | 4.7782 | 7.092
3000 | 50 | [12 empty] | 13.416 | 5.8078 | 7.88
3600 | 60 | [12 empty] | 18.8047 | 8.1406 | 9.456
4200 | 70
4800 | 80
5400 | 90
6000 | 100
7500 | 125
9000 | 150
10500 | 175
12000 | 200
| Note: Values in shaded areas are at velocities over 5 fps | [7 empty] | H = 10.44 * L * (Q/C)1.852 * D-4.871 |  |  |  | H (feet) = Pressure loss
| (feet per second) and should be selected with caution. | [11 empty] | Q (gpm) = Flow in pipe segment
D (inches) = Actual pipe inside diameter
L (feet) = Pipe length ( = 100 for table)
C is a constant ( = 150 used for PVC)
Table 1b:
Pressure Loss per 100-feet of Schedule 40 PVC and Velocity
as a function of flow rate and nominal pipe diameter in inches
|  | 2 |  |  | 2.5 |  |  | 3 |  |  | 4 |  |  | 6
Flow |  | Pressure Drop |  | Velocity | Pressure Drop |  | Velocity | Pressure Drop |  | Velocity | Pressure Drop |  | Velocity | Pressure Drop |  | Velocity
gph | gpm | feet | psi | fps | feet | psi | fps | feet | psi | fps | feet | psi | fps | feet | psi | fps
60 | 1
120 | 2
180 | 3
240 | 4
300 | 5
360 | 6 | 0.078287 | 0.033891 | 0.57369
480 | 8 | 0.13338 | 0.057739 | 0.76492
600 | 10 | 0.20163 | 0.087286 | 0.95615 | 0.084842 | 0.036728 | 0.67014
900 | 15 | 0.42725 | 0.18495 | 1.4342 | 0.17978 | 0.077825 | 1.0052 | 0.062406 | 0.027016 | 0.65101
1200 | 20 | 0.72789 | 0.3151 | 1.9123 | 0.30628 | 0.13259 | 1.3403 | 0.10632 | 0.046026 | 0.86801
1500 | 25 | 1.1004 | 0.47635 | 2.3904 | 0.46301 | 0.20044 | 1.6753 | 0.16073 | 0.069579 | 1.085
1800 | 30 | 1.5424 | 0.66769 | 2.8685 | 0.64899 | 0.28095 | 2.0104 | 0.22529 | 0.097527 | 1.302 | 0.059961 | 0.025957 | 0.7561
2100 | 35 | 2.052 | 0.8883 | 3.3465 | 0.86342 | 0.37378 | 2.3455 | 0.29972 | 0.12975 | 1.519 | 0.079773 | 0.034534 | 0.88212
2400 | 40 | 2.6277 | 1.1375 | 3.8246 | 1.1057 | 0.47864 | 2.6806 | 0.38382 | 0.16615 | 1.736 | 0.10215 | 0.044222 | 1.0081
2700 | 45 | 3.2682 | 1.4148 | 4.3027 | 1.3752 | 0.59532 | 3.0156 | 0.47737 | 0.20665 | 1.953 | 0.12705 | 0.055002 | 1.1342
3000 | 50 | 3.9724 | 1.7196 | 4.7808 | 1.6715 | 0.72359 | 3.3507 | 0.58023 | 0.25118 | 2.17 | 0.15443 | 0.066853 | 1.2602
3600 | 60 | 5.5679 | 2.4104 | 5.7369 | 2.3429 | 1.0142 | 4.0208 | 0.81329 | 0.35207 | 2.604 | 0.21646 | 0.093705 | 1.5122
4200 | 70 | 7.4076 | 3.2068 | 6.6931 | 3.117 | 1.3493 | 4.691 | 1.082 | 0.4684 | 3.0381 | 0.28798 | 0.12467 | 1.7642
4800 | 80 | 9.4859 | 4.1065 | 7.6492 | 3.9915 | 1.7279 | 5.3611 | 1.3856 | 0.59982 | 3.4721 | 0.36878 | 0.15964 | 2.0163
5400 | 90 | 11.7981 | 5.1074 | 8.6054 | 4.9644 | 2.1491 | 6.0313 | 1.7233 | 0.74602 | 3.9061 | 0.45867 | 0.19856 | 2.2683 | 0.062326 | 0.026981 | 0.99951
6000 | 100 | 14.3402 | 6.2079 | 9.5615 | 6.0341 | 2.6121 | 6.7014 | 2.0946 | 0.90677 | 4.3401 | 0.55749 | 0.24134 | 2.5203 | 0.075755 | 0.032794 | 1.1106
7500 | 125 |  |  |  | 9.1219 | 3.9489 | 8.3767 | 3.1665 | 1.3708 | 5.4251 | 0.84278 | 0.36484 | 3.1504 | 0.11452 | 0.049577 | 1.3882
9000 | 150 |  |  |  | 12.7859 | 5.535 | 10.0521 | 4.4384 | 1.9214 | 6.5101 | 1.1813 | 0.51139 | 3.7805 | 0.16052 | 0.06949 | 1.6659
10500 | 175 | [6 empty] | 5.9049 | 2.5562 | 7.5951 | 1.5716 | 0.68035 | 4.4106 | 0.21356 | 0.09245 | 1.9435
12000 | 200 | [6 empty] | 7.5616 | 3.2734 | 8.6801 | 2.0126 | 0.87123 | 5.0407 | 0.27348 | 0.11839 | 2.2211
| Note: Values in shaded areas are at velocities over 5 fps | [7 empty] | H = 10.44 * L * (Q/C)1.852 * D-4.871 |  |  |  | H (feet) = Pressure loss
| (feet per second) and should be selected with caution. | [11 empty] | Q (gpm) = Flow in pipe segment
D (inches) = Actual pipe inside diameter
L (feet) = Pipe length ( = 100' for table)
C is a constant ( = 150 used for PVC)
Table 2:
Orifice Flow Rate in gallons per minute (gpm)
as a function of pressure head and drilled hole diameter in PVC pipe
Pressure Head | [5 empty] | Orifice diameter (inches)
feet | psi | 0.125 | 0.15625 | 0.1875 | 0.21875 | 0.25 | 0.28125 | 0.3125 | 0.34375 | 0.375 | 0.40625 | 0.4375 | 0.46875 | 0.5 | 0.5625 | 0.625 | 0.6875 | 0.75
1 | 0.4329 | 0.18422 | 0.28784 | 0.41449 | 0.56417 | 0.73687 | 0.93261 | 1.1514 | 1.3932 | 1.658 | 1.9458 | 2.2567 | 2.5906 | 2.9475 | 3.7304 | 4.6055 | 5.5726 | 6.6319
1.5 | 0.64935 | 0.22562 | 0.35253 | 0.50765 | 0.69096 | 0.90248 | 1.1422 | 1.4101 | 1.7063 | 2.0306 | 2.3831 | 2.7639 | 3.1728 | 3.6099 | 4.5688 | 5.6405 | 6.825 | 8.1224
2 | 0.8658 | 0.26052 | 0.40707 | 0.58618 | 0.79786 | 1.0421 | 1.3189 | 1.6283 | 1.9702 | 2.3447 | 2.7518 | 3.1914 | 3.6636 | 4.1684 | 5.2756 | 6.5131 | 7.8809 | 9.3789
2.5 | 1.0823 | 0.29128 | 0.45512 | 0.65537 | 0.89203 | 1.1651 | 1.4746 | 1.8205 | 2.2028 | 2.6215 | 3.0766 | 3.5681 | 4.0961 | 4.6604 | 5.8983 | 7.2819 | 8.8111 | 10.4859
3 | 1.2987 | 0.31908 | 0.49856 | 0.71792 | 0.97717 | 1.2763 | 1.6153 | 1.9942 | 2.413 | 2.8717 | 3.3702 | 3.9087 | 4.487 | 5.1052 | 6.4613 | 7.9769 | 9.6521 | 11.4867
3.5 | 1.5152 | 0.34464 | 0.5385 | 0.77544 | 1.0555 | 1.3786 | 1.7447 | 2.154 | 2.6064 | 3.1018 | 3.6403 | 4.2219 | 4.8465 | 5.5143 | 6.979 | 8.616 | 10.4254 | 12.4071
4 | 1.7316 | 0.36844 | 0.57568 | 0.82898 | 1.1283 | 1.4737 | 1.8652 | 2.3027 | 2.7863 | 3.3159 | 3.8916 | 4.5134 | 5.1812 | 5.895 | 7.4609 | 9.2109 | 11.1452 | 13.2637
4.5 | 1.9481 | 0.39079 | 0.6106 | 0.87927 | 1.1968 | 1.5631 | 1.9784 | 2.4424 | 2.9553 | 3.5171 | 4.1277 | 4.7871 | 5.4954 | 6.2526 | 7.9134 | 9.7697 | 11.8213 | 14.0683
5 | 2.1645 | 0.41193 | 0.64363 | 0.92683 | 1.2615 | 1.6477 | 2.0854 | 2.5745 | 3.1152 | 3.7073 | 4.351 | 5.0461 | 5.7927 | 6.5908 | 8.3415 | 10.2981 | 12.4608 | 14.8293
| psi = pounds per square inch |  |  |  | Q = 11.79 * D2 * √h |  |  | Q (gpm) = Flow through orifice
D (inches) = Orifice diameter
h (feet) = Pressure head at orifice
Table 3:
Nominal Pipe Diameter to Actual Inside Diameter Conversion (inches)
Pipe Class/ Schedule
|  | 0.5 | 0.75 | 1 | 1.25 | 1.5 | 2 | 2.5 | 3 | 4 | 6 |  | SUPPLY ID
125 |  | NA | NA | NA | 1.548 | 1.784 | 2.229 | NA | 3.284 | 4.224 | 6.217 |  | #N/A
160 |  | NA | NA | NA | 1.532 | 1.754 | 2.193 | 2.655 | 3.23 | 4.154 | 6.115 |  | Col
200 |  | NA | 0.93 | 1.189 | 1.502 | 1.72 | 2.149 | 2.601 | 3.166 | 4.072 | 5.993 |  | #N/A
315 |  | 0.716 | 0.894 | 1.121 | 1.414 | 1.618 | 2.023 | 2.449 | 2.962 | 3.834 | 5.643 |  | Row
40 |  | 0.622 | 0.824 | 1.049 | 1.38 | 1.61 | 2.067 | 2.469 | 3.068 | 4.026 | 6.065 |  | 4
80 |  | 0.546 | 0.742 | 0.957 | 1.278 | 1.5 | 1.939 | 2.323 | 2.9 | 3.826 | 5.761
Table 4
Flow Rate (gpm) Needed to Effectively Scour Schedule 40 Pipe
|  | Nominal Pipe Diameter (inches) |  |  | gpm for 2 fps (minimum recommended) |  |  | gpm for 5 fps (maximum recommended)
|  |  | 1 |  |  | 5.381 |  |  | 13.4689
|  |  | 1.25 |  |  | 9.3125 |  |  | 23.3099
|  |  | 1.5 |  |  | 12.6754 |  |  | 31.7273
|  |  | 2 |  |  | 20.8925 |  |  | 52.2953
|  |  | 2.5 |  |  | 29.8092 |  |  | 74.6146
|  |  | 3 |  |  | 46.0277 |  |  | 115.2105
2 fps is the generally accepted minimum pipe scouring velocity
Table 5:
Pipe storage capacity - gallons per 100-feet
as a function of nominal pipe diameter and class/ schedule
Pipe Class/ Schedule |  |  |  |  | Diameter (inches)
|  | 0.5 | 0.75 | 1 | 1.25 | 1.5 | 2 | 2.5 | 3 | 4 | 6
125 |  | NA | NA | NA | 9.7769 | 12.9852 | 20.2712 | NA | 44.0014 | 72.7961 | 157.6964
160 |  | NA | NA | NA | 9.5759 | 12.5522 | 19.6217 | 28.76 | 42.5662 | 70.4033 | 152.5644
200 |  | NA | 3.5288 | 5.768 | 9.2045 | 12.0703 | 18.8423 | 27.602 | 40.8961 | 67.6512 | 146.5375
315 |  | 2.0916 | 3.2609 | 5.1271 | 8.1575 | 10.6811 | 16.6975 | 24.4702 | 35.7957 | 59.9742 | 129.9213
40 |  | 1.5785 | 2.7702 | 4.4896 | 7.77 | 10.5758 | 17.4318 | 24.8715 | 38.4035 | 66.1314 | 150.0796
80 |  | 1.2163 | 2.2463 | 3.7367 | 6.6638 | 9.18 | 15.3397 | 22.017 | 34.3128 | 59.7242 | 135.4116
|  |  |  | V = π * (D/24)2*L*7.48 |  |  | V (gallons) = Pipe volume
|  |  |  | = 0.0408 * (D)2*L |  |  | D (inches) = Inside Diameter
L (feet) = Pipe length ( = 100' for table)